## Slide 1
Photovoltaic Inverter Model in Simulink
EE 435 Design Project
Corey B. and Samuel T. (G-5)

## Slide 2: Introduction
NREL Solar District Cup competition
Designed Solar+Storage system for New Mexico State University
For EE 435, we re-designed one of the “Grid-tie-ready” PV Inverters
  Currently net metering not permitted
MOSFET H-bridge design

## Slide 3: Application in Question
Corbett Center Rooftop (NMSU's “Mountainlair”)
278.2 kWDC
Canadian Solar 420W Modules
20% Bifacial Gain
SMA Sunny Tripower Core-1 String

## Slide 4: Goal: Redesign One of System’s Inverters
System Specifications
MOSFET H-Bridge Inputs:
  = 127 A
  = 155 A
  = 632 V
  = 883 V
  = 80 kW
  = 137 kW
Thermal Specifications:
  < 0.2818

## Slide 5: Notable Specs of Selected Devices
PV module: CS32-420PB-AG
= 39.5 V
= 10.64 A
= 48 V
= 11.26 A
MOSFETs: C2M0025120D
= 1200 V
= 90 A
= 25 mΩ
= 0.27
= 40
Heatsink: Fischer Elektronik LA 6/100 12V
= 0.2

## Slide 6: Performance Additions
DC-link capacitor
  Pre-inverter filter to smooth DC signal
LC filter
  Resonant filter following H-bridge
  Reduces distortion in sinusoidal output
  Unfortunately provides marginal attenuation of output current

## Slide 7: Device Protection Considerations
Heat sink
  Improve lifetime of active devices
  Reduce risk of destroying devices during max load
RC Snubber Circuits
  Mitigates against transient events
  di/dt and dv/dt protection
Anti-islanding
  Useful once grid-tie permitted at NMSU
RC Snubber Circuit

## Slide 8: Overall Circuit Topology

## Slide 9: Control Scheme
Phase Lock Loop
  Extract frequency from output
Park Transform (abc→dq0)
  Extract peak value of output
PID controller
  Multiplies PID gains by the error between desired peak and current peak calculated by Park Transform
  Output (ma) is multiplied with 3-phase unit sinusoids and then input into two-level PWM generator

## Slide 10: Pulse Width Modulation (PWM) Scheme
Sawtooth carrier signal
  Compared against modulating signal
Two-level PWM
  is 3 phase input
  When is greater than carrier, the pulse for upper switching device is 1 and lower switching device is 0
Two Level PWM Scheme Summary
Modulated Inverter Output

## Slide 11: Simulation Results
Light Rated Heavy
From top to bottom, vs. time: 1. Phase-to-phase output voltages, 2. Phase currents, 3. THD

## Slide 12: Future Work
Maximum Power Point Tracking
  Maximize power utilized from source
  Senses voltage and current, provides feedback to converter
  Algorithmic (e.g. perturb/observe)
DC Gain Stage
  Necessary for grid-tie operation
  Push-pull converter considered
Improve output voltage regulation
  Research superior control system
  Grid-tie typically fixed-current control instead of fixed-voltage control

## Slide 13: Thank you!
… any questions?